## METERS
Site | Room | Meter_ID | Meter_Name | Meter_Role | Energy_Domain | Equipment_Type | Manufacturer | Model | Serial | IP_Address | Parent_Meter_ID | Measurement_Boundary | Unit | Status | Notes
DC-DEMO | Energy Center | MTR-TF-01 | Transformer T1 | TOTAL_FACILITY | FACILITY | TRANSFORMER | Siemens | Sentron PAC4200 | TF01-SYN | 10.20.1.11 |  | MAIN_PUE | kWh | ACTIVE | Synthetic demo
DC-DEMO | Energy Center | MTR-TF-02 | Transformer T2 | TOTAL_FACILITY | FACILITY | TRANSFORMER | Siemens | Sentron PAC4200 | TF02-SYN | 10.20.1.12 |  | MAIN_PUE | kWh | ACTIVE | Synthetic demo
DC-DEMO | IT Electrical Room | MTR-IT-A | IT Board A | IT_ENERGY | IT | SWITCHBOARD | Schneider Electric | PowerLogic PM8000 | ITA-SYN | 10.20.2.11 | MTR-TF-01 | MAIN_PUE | kWh | ACTIVE | Synthetic demo
DC-DEMO | IT Electrical Room | MTR-IT-B | IT Board B | IT_ENERGY | IT | SWITCHBOARD | Schneider Electric | PowerLogic PM8000 | ITB-SYN | 10.20.2.12 | MTR-TF-02 | MAIN_PUE | kWh | ACTIVE | Synthetic demo
DC-DEMO | IT Electrical Room | MTR-IT-C | IT Board C | IT_ENERGY | IT | UPS_OUTPUT | Eaton | 93PM Meter | ITC-SYN | 10.20.2.13 | MTR-TF-02 | MAIN_PUE | kWh | ACTIVE | Synthetic demo
DC-DEMO | Cooling Plant | MTR-CL-01 | Chiller Plant | COOLING | COOLING | CHILLER_METER | Siemens | Sentron PAC4200 | CL01-SYN | 10.20.3.11 | MTR-TF-01 | MAIN_PUE | kWh | ACTIVE | Synthetic demo
DC-DEMO | White Space | MTR-CL-02 | CRAC and InRow | COOLING | COOLING | COOLING_PANEL | Schneider Electric | PowerLogic PM5000 | CL02-SYN | 10.20.3.12 | MTR-TF-02 | MAIN_PUE | kWh | ACTIVE | Synthetic demo
DC-DEMO | Utility Area | MTR-AUX-01 | Auxiliary Services | AUXILIARY | FACILITY | SWITCHBOARD | Schneider Electric | PowerLogic PM5000 | AUX-SYN | 10.20.4.11 | MTR-TF-01 | MAIN_PUE | kWh | ACTIVE | Synthetic demo

## READINGS
Reading_ID | Meter_ID | Period_Start | Period_End | Reading_Type | Energy_kWh | Average_Power_kW | Peak_Power_kW | Source | Quality_Status | Comments
RDG-01-MTR-TF-01 | MTR-TF-01 | 2025-01-01 | 2025-01-31 | INTERVAL_CONSUMPTION | 669982.4 | 900.51 | 1044.6 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-01-MTR-TF-02 | MTR-TF-02 | 2025-01-01 | 2025-01-31 | INTERVAL_CONSUMPTION | 643708.6 | 865.2 | 1003.63 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-01-MTR-IT-A | MTR-IT-A | 2025-01-01 | 2025-01-31 | INTERVAL_CONSUMPTION | 327060 | 439.6 | 509.93 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-01-MTR-IT-B | MTR-IT-B | 2025-01-01 | 2025-01-31 | INTERVAL_CONSUMPTION | 308890 | 415.17 | 481.6 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-01-MTR-IT-C | MTR-IT-C | 2025-01-01 | 2025-01-31 | INTERVAL_CONSUMPTION | 272550 | 366.33 | 424.94 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-01-MTR-CL-01 | MTR-CL-01 | 2025-01-01 | 2025-01-31 | INTERVAL_CONSUMPTION | 210699.3 | 283.2 | 328.51 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-01-MTR-CL-02 | MTR-CL-02 | 2025-01-01 | 2025-01-31 | INTERVAL_CONSUMPTION | 125609.2 | 168.83 | 195.84 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-01-MTR-AUX-01 | MTR-AUX-01 | 2025-01-01 | 2025-01-31 | INTERVAL_CONSUMPTION | 68882.5 | 92.58 | 107.4 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-02-MTR-TF-01 | MTR-TF-01 | 2025-02-01 | 2025-02-28 | INTERVAL_CONSUMPTION | 675783.2 | 1005.63 | 1166.53 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-02-MTR-TF-02 | MTR-TF-02 | 2025-02-01 | 2025-02-28 | INTERVAL_CONSUMPTION | 649281.8 | 966.19 | 1120.78 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-02-MTR-IT-A | MTR-IT-A | 2025-02-01 | 2025-02-28 | INTERVAL_CONSUMPTION | 330120 | 491.25 | 569.85 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-02-MTR-IT-B | MTR-IT-B | 2025-02-01 | 2025-02-28 | INTERVAL_CONSUMPTION | 311780 | 463.96 | 538.19 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-02-MTR-IT-C | MTR-IT-C | 2025-02-01 | 2025-02-28 | INTERVAL_CONSUMPTION | 275100 | 409.38 | 474.87 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-02-MTR-CL-01 | MTR-CL-01 | 2025-02-01 | 2025-02-28 | INTERVAL_CONSUMPTION | 212193.8 | 315.76 | 366.29 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-02-MTR-CL-02 | MTR-CL-02 | 2025-02-01 | 2025-02-28 | INTERVAL_CONSUMPTION | 126500.1 | 188.24 | 218.36 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-02-MTR-AUX-01 | MTR-AUX-01 | 2025-02-01 | 2025-02-28 | INTERVAL_CONSUMPTION | 69371.1 | 103.23 | 119.75 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-03-MTR-TF-01 | MTR-TF-01 | 2025-03-01 | 2025-03-31 | INTERVAL_CONSUMPTION | 681575.2 | 916.1 | 1062.67 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-03-MTR-TF-02 | MTR-TF-02 | 2025-03-01 | 2025-03-31 | INTERVAL_CONSUMPTION | 654846.8 | 880.17 | 1021 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-03-MTR-IT-A | MTR-IT-A | 2025-03-01 | 2025-03-31 | INTERVAL_CONSUMPTION | 333180 | 447.82 | 519.47 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-03-MTR-IT-B | MTR-IT-B | 2025-03-01 | 2025-03-31 | INTERVAL_CONSUMPTION | 314670 | 422.94 | 490.61 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-03-MTR-IT-C | MTR-IT-C | 2025-03-01 | 2025-03-31 | INTERVAL_CONSUMPTION | 277650 | 373.19 | 432.9 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-03-MTR-CL-01 | MTR-CL-01 | 2025-03-01 | 2025-03-31 | INTERVAL_CONSUMPTION | 213679.4 | 287.2 | 333.16 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-03-MTR-CL-02 | MTR-CL-02 | 2025-03-01 | 2025-03-31 | INTERVAL_CONSUMPTION | 127385.8 | 171.22 | 198.61 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-03-MTR-AUX-01 | MTR-AUX-01 | 2025-03-01 | 2025-03-31 | INTERVAL_CONSUMPTION | 69856.7 | 93.89 | 108.92 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-04-MTR-TF-01 | MTR-TF-01 | 2025-04-01 | 2025-04-30 | INTERVAL_CONSUMPTION | 687358.6 | 954.66 | 1107.41 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-04-MTR-TF-02 | MTR-TF-02 | 2025-04-01 | 2025-04-30 | INTERVAL_CONSUMPTION | 660403.4 | 917.23 | 1063.98 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-04-MTR-IT-A | MTR-IT-A | 2025-04-01 | 2025-04-30 | INTERVAL_CONSUMPTION | 336240 | 467 | 541.72 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-04-MTR-IT-B | MTR-IT-B | 2025-04-01 | 2025-04-30 | INTERVAL_CONSUMPTION | 317560 | 441.06 | 511.62 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-04-MTR-IT-C | MTR-IT-C | 2025-04-01 | 2025-04-30 | INTERVAL_CONSUMPTION | 280200 | 389.17 | 451.43 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-04-MTR-CL-01 | MTR-CL-01 | 2025-04-01 | 2025-04-30 | INTERVAL_CONSUMPTION | 215156.2 | 298.83 | 346.64 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-04-MTR-CL-02 | MTR-CL-02 | 2025-04-01 | 2025-04-30 | INTERVAL_CONSUMPTION | 128266.2 | 178.15 | 206.65 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-04-MTR-AUX-01 | MTR-AUX-01 | 2025-04-01 | 2025-04-30 | INTERVAL_CONSUMPTION | 70339.5 | 97.69 | 113.32 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-05-MTR-TF-01 | MTR-TF-01 | 2025-05-01 | 2025-05-31 | INTERVAL_CONSUMPTION | 693133.4 | 931.63 | 1080.69 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-05-MTR-TF-02 | MTR-TF-02 | 2025-05-01 | 2025-05-31 | INTERVAL_CONSUMPTION | 665951.7 | 895.1 | 1038.31 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-05-MTR-IT-A | MTR-IT-A | 2025-05-01 | 2025-05-31 | INTERVAL_CONSUMPTION | 339300 | 456.05 | 529.02 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-05-MTR-IT-B | MTR-IT-B | 2025-05-01 | 2025-05-31 | INTERVAL_CONSUMPTION | 320450 | 430.71 | 499.63 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-05-MTR-IT-C | MTR-IT-C | 2025-05-01 | 2025-05-31 | INTERVAL_CONSUMPTION | 282750 | 380.04 | 440.85 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-05-MTR-CL-01 | MTR-CL-01 | 2025-05-01 | 2025-05-31 | INTERVAL_CONSUMPTION | 216624.2 | 291.16 | 337.75 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-05-MTR-CL-02 | MTR-CL-02 | 2025-05-01 | 2025-05-31 | INTERVAL_CONSUMPTION | 129141.4 | 173.58 | 201.35 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-05-MTR-AUX-01 | MTR-AUX-01 | 2025-05-01 | 2025-05-31 | INTERVAL_CONSUMPTION | 70819.5 | 95.19 | 110.42 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-06-MTR-TF-01 | MTR-TF-01 | 2025-06-01 | 2025-06-30 | INTERVAL_CONSUMPTION | 698899.4 | 970.69 | 1126 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-06-MTR-TF-02 | MTR-TF-02 | 2025-06-01 | 2025-06-30 | INTERVAL_CONSUMPTION | 671491.6 | 932.63 | 1081.85 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-06-MTR-IT-A | MTR-IT-A | 2025-06-01 | 2025-06-30 | INTERVAL_CONSUMPTION | 342360 | 475.5 | 551.58 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-06-MTR-IT-B | MTR-IT-B | 2025-06-01 | 2025-06-30 | INTERVAL_CONSUMPTION | 323340 | 449.08 | 520.94 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-06-MTR-IT-C | MTR-IT-C | 2025-06-01 | 2025-06-30 | INTERVAL_CONSUMPTION | 285300 | 396.25 | 459.65 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-06-MTR-CL-01 | MTR-CL-01 | 2025-06-01 | 2025-06-30 | INTERVAL_CONSUMPTION | 218083.3 | 302.89 | 351.36 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-06-MTR-CL-02 | MTR-CL-02 | 2025-06-01 | 2025-06-30 | INTERVAL_CONSUMPTION | 130011.2 | 180.57 | 209.46 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-06-MTR-AUX-01 | MTR-AUX-01 | 2025-06-01 | 2025-06-30 | INTERVAL_CONSUMPTION | 71296.5 | 99.02 | 114.87 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-07-MTR-TF-01 | MTR-TF-01 | 2025-07-01 | 2025-07-31 | INTERVAL_CONSUMPTION | 704656.8 | 947.12 | 1098.66 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-07-MTR-TF-02 | MTR-TF-02 | 2025-07-01 | 2025-07-31 | INTERVAL_CONSUMPTION | 677023.2 | 909.98 | 1055.57 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-07-MTR-IT-A | MTR-IT-A | 2025-07-01 | 2025-07-31 | INTERVAL_CONSUMPTION | 345420 | 464.27 | 538.56 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-07-MTR-IT-B | MTR-IT-B | 2025-07-01 | 2025-07-31 | INTERVAL_CONSUMPTION | 326230 | 438.48 | 508.64 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-07-MTR-IT-C | MTR-IT-C | 2025-07-01 | 2025-07-31 | INTERVAL_CONSUMPTION | 287850 | 386.9 | 448.8 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-07-MTR-CL-01 | MTR-CL-01 | 2025-07-01 | 2025-07-31 | INTERVAL_CONSUMPTION | 219533.6 | 295.07 | 342.28 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-07-MTR-CL-02 | MTR-CL-02 | 2025-07-01 | 2025-07-31 | INTERVAL_CONSUMPTION | 130875.8 | 175.91 | 204.05 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-07-MTR-AUX-01 | MTR-AUX-01 | 2025-07-01 | 2025-07-31 | INTERVAL_CONSUMPTION | 71770.6 | 96.47 | 111.9 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-08-MTR-TF-01 | MTR-TF-01 | 2025-08-01 | 2025-08-31 | INTERVAL_CONSUMPTION | 711392.9 | 956.17 | 1109.16 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-08-MTR-TF-02 | MTR-TF-02 | 2025-08-01 | 2025-08-31 | INTERVAL_CONSUMPTION | 683495.1 | 918.68 | 1065.66 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-08-MTR-IT-A | MTR-IT-A | 2025-08-01 | 2025-08-31 | INTERVAL_CONSUMPTION | 348480 | 468.39 | 543.33 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-08-MTR-IT-B | MTR-IT-B | 2025-08-01 | 2025-08-31 | INTERVAL_CONSUMPTION | 329120 | 442.37 | 513.14 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-08-MTR-IT-C | MTR-IT-C | 2025-08-01 | 2025-08-31 | INTERVAL_CONSUMPTION | 290400 | 390.32 | 452.77 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-08-MTR-CL-01 | MTR-CL-01 | 2025-08-01 | 2025-08-31 | INTERVAL_CONSUMPTION | 221981.8 | 298.36 | 346.1 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-08-MTR-CL-02 | MTR-CL-02 | 2025-08-01 | 2025-08-31 | INTERVAL_CONSUMPTION | 132335.3 | 177.87 | 206.33 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-08-MTR-AUX-01 | MTR-AUX-01 | 2025-08-01 | 2025-08-31 | INTERVAL_CONSUMPTION | 72571 | 97.54 | 113.15 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-09-MTR-TF-01 | MTR-TF-01 | 2025-09-01 | 2025-09-30 | INTERVAL_CONSUMPTION | 718137.6 | 997.41 | 1157 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-09-MTR-TF-02 | MTR-TF-02 | 2025-09-01 | 2025-09-30 | INTERVAL_CONSUMPTION | 689975.4 | 958.3 | 1111.63 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-09-MTR-IT-A | MTR-IT-A | 2025-09-01 | 2025-09-30 | INTERVAL_CONSUMPTION | 351540 | 488.25 | 566.37 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-09-MTR-IT-B | MTR-IT-B | 2025-09-01 | 2025-09-30 | INTERVAL_CONSUMPTION | 332010 | 461.12 | 534.9 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-09-MTR-IT-C | MTR-IT-C | 2025-09-01 | 2025-09-30 | INTERVAL_CONSUMPTION | 292950 | 406.88 | 471.97 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-09-MTR-CL-01 | MTR-CL-01 | 2025-09-01 | 2025-09-30 | INTERVAL_CONSUMPTION | 224438.8 | 311.72 | 361.6 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-09-MTR-CL-02 | MTR-CL-02 | 2025-09-01 | 2025-09-30 | INTERVAL_CONSUMPTION | 133800 | 185.83 | 215.57 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-09-MTR-AUX-01 | MTR-AUX-01 | 2025-09-01 | 2025-09-30 | INTERVAL_CONSUMPTION | 73374.2 | 101.91 | 118.21 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-10-MTR-TF-01 | MTR-TF-01 | 2025-10-01 | 2025-10-31 | INTERVAL_CONSUMPTION | 724891.1 | 974.32 | 1130.21 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-10-MTR-TF-02 | MTR-TF-02 | 2025-10-01 | 2025-10-31 | INTERVAL_CONSUMPTION | 696463.9 | 936.11 | 1085.88 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-10-MTR-IT-A | MTR-IT-A | 2025-10-01 | 2025-10-31 | INTERVAL_CONSUMPTION | 354600 | 476.61 | 552.87 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-10-MTR-IT-B | MTR-IT-B | 2025-10-01 | 2025-10-31 | INTERVAL_CONSUMPTION | 334900 | 450.13 | 522.16 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-10-MTR-IT-C | MTR-IT-C | 2025-10-01 | 2025-10-31 | INTERVAL_CONSUMPTION | 295500 | 397.18 | 460.73 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-10-MTR-CL-01 | MTR-CL-01 | 2025-10-01 | 2025-10-31 | INTERVAL_CONSUMPTION | 226904.6 | 304.98 | 353.78 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-10-MTR-CL-02 | MTR-CL-02 | 2025-10-01 | 2025-10-31 | INTERVAL_CONSUMPTION | 135270 | 181.81 | 210.9 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-10-MTR-AUX-01 | MTR-AUX-01 | 2025-10-01 | 2025-10-31 | INTERVAL_CONSUMPTION | 74180.4 | 99.7 | 115.66 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-11-MTR-TF-01 | MTR-TF-01 | 2025-11-01 | 2025-11-30 | INTERVAL_CONSUMPTION | 731653.1 | 1016.18 | 1178.77 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-11-MTR-TF-02 | MTR-TF-02 | 2025-11-01 | 2025-11-30 | INTERVAL_CONSUMPTION | 702960.9 | 976.33 | 1132.55 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-11-MTR-IT-A | MTR-IT-A | 2025-11-01 | 2025-11-30 | INTERVAL_CONSUMPTION | 357660 | 496.75 | 576.23 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-11-MTR-IT-B | MTR-IT-B | 2025-11-01 | 2025-11-30 | INTERVAL_CONSUMPTION | 337790 | 469.15 | 544.22 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-11-MTR-IT-C | MTR-IT-C | 2025-11-01 | 2025-11-30 | INTERVAL_CONSUMPTION | 298050 | 413.96 | 480.19 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-11-MTR-CL-01 | MTR-CL-01 | 2025-11-01 | 2025-11-30 | INTERVAL_CONSUMPTION | 229379.3 | 318.58 | 369.56 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-11-MTR-CL-02 | MTR-CL-02 | 2025-11-01 | 2025-11-30 | INTERVAL_CONSUMPTION | 136745.3 | 189.92 | 220.31 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-11-MTR-AUX-01 | MTR-AUX-01 | 2025-11-01 | 2025-11-30 | INTERVAL_CONSUMPTION | 74989.4 | 104.15 | 120.82 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-12-MTR-TF-01 | MTR-TF-01 | 2025-12-01 | 2025-12-31 | INTERVAL_CONSUMPTION | 738423.9 | 992.51 | 1151.31 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-12-MTR-TF-02 | MTR-TF-02 | 2025-12-01 | 2025-12-31 | INTERVAL_CONSUMPTION | 709466.1 | 953.58 | 1106.16 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-12-MTR-IT-A | MTR-IT-A | 2025-12-01 | 2025-12-31 | INTERVAL_CONSUMPTION | 360720 | 484.84 | 562.41 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-12-MTR-IT-B | MTR-IT-B | 2025-12-01 | 2025-12-31 | INTERVAL_CONSUMPTION | 340680 | 457.9 | 531.17 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-12-MTR-IT-C | MTR-IT-C | 2025-12-01 | 2025-12-31 | INTERVAL_CONSUMPTION | 300600 | 404.03 | 468.68 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-12-MTR-CL-01 | MTR-CL-01 | 2025-12-01 | 2025-12-31 | INTERVAL_CONSUMPTION | 231862.8 | 311.64 | 361.51 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-12-MTR-CL-02 | MTR-CL-02 | 2025-12-01 | 2025-12-31 | INTERVAL_CONSUMPTION | 138225.9 | 185.79 | 215.51 | DEMO_IMPORT | VALIDATED | Synthetic demo
RDG-12-MTR-AUX-01 | MTR-AUX-01 | 2025-12-01 | 2025-12-31 | INTERVAL_CONSUMPTION | 75801.3 | 101.88 | 118.18 | DEMO_IMPORT | VALIDATED | Synthetic demo

## BOUNDARIES
Boundary_ID | Boundary_Name | Meter_ID | PUE_Component | Sign | Valid_From | Valid_To | Notes
BND-001 | Main PUE | MTR-TF-01 | TOTAL_FACILITY | 1 | 2025-01-01 |  | Synthetic demo
BND-002 | Main PUE | MTR-TF-02 | TOTAL_FACILITY | 1 | 2025-01-01 |  | Synthetic demo
BND-003 | Main PUE | MTR-IT-A | IT_ENERGY | 1 | 2025-01-01 |  | Synthetic demo
BND-004 | Main PUE | MTR-IT-B | IT_ENERGY | 1 | 2025-01-01 |  | Synthetic demo
BND-005 | Main PUE | MTR-IT-C | IT_ENERGY | 1 | 2025-01-01 |  | Synthetic demo
BND-006 | Main PUE | MTR-CL-01 | COOLING | 1 | 2025-01-01 |  | Synthetic demo
BND-007 | Main PUE | MTR-CL-02 | COOLING | 1 | 2025-01-01 |  | Synthetic demo

## TARGETS
Target_ID | Site | Period | Target_PUE | Baseline_PUE | Target_Overhead_Percent | Notes
TGT-001 | DC-DEMO | 2026 | 1.35 | 1.48 | 25.9 | Operational target
TGT-002 | DC-DEMO | 2027 | 1.30 | 1.35 | 23.1 | Planning scenario